## Tabelle1
Cirucuit | Sensor name | Sensor ID | name | Seeweg Sensor IDs | Cirucuit M | Sensor name M | Sensor ID M | name M | Mendelstraße Sensor IDs
Tank | tank pos1 top TSPO 2441 | 2441 | t_sp1 | 2441 | Tank Loading | tank top superior TLSPos pos1 4244 | 4244 | t_lsp1 | 4244
| tank pos6 middle TSPM 2434 | 2434 | t_sp3 | 2434 |  | tank top inferior TLSPo pos 3 4238 | 4238 | t_lsp2 | 4238
| tank pos11 bottom TSPU 2448 | 2448 | t_sp6 | 2448 |  | tank middle TLSPm pos6 4232 | 4232 | t_lsp3 | 4232
| tank pos 4 | 13211 | t_sp2 | 13211 |  | tank bottom TLSPu pos11 4250 | 4250 | t_lsp5 | 4250
| tank pos 7 | 13210 | t_sp4 | 13210 |  | tank pos 9 | 14110 | t_lsp4 | 14110
| tank pos 9 | 13209 | t_sp5 | 13209 | Tank Solar | tank top inferior TSSPo pos1 4358 | 4358 | t_ssp1 | 4358
HK1 | feedflow TVV1 3359 | 3359 | t_hc1_feedflow | 3359 |  | tank middle TSSPm pos6 4352 | 4352 | t_ssp3 | 4352
| flow TVH1 2469 | 2469 | t_hc1_flow | 2469 |  | tank bottom TSSPu pos11 4346 | 4346 | t_ssp5 | 4346
| return TRH1 2350 | 2350 | t_hc1_return | 2350 |  | tank pos 3 | 14104 | t_ssp2 | 14104
| vdot VZHK1 2577 | 2577 | vdot_hc1_feedflow | 2577 |  | tank pos 9 | 14105 | t_ssp4 | 14105
| Ventilstellung RV_HK1 2569 | 2569 | vent_hc1 | 2569 | HK1 | flow TVHK1 4370 | 4370 | t_hc1_flow | 4370
HK2 | feedflow TVV2 2532 | 2532 | t_hc2_feedflow | 2532 |  | return TRHK1 4262 | 4262 | t_hc1_return | 4262
| flow TVH2 2476 | 2476 | t_hc2_flow | 2476 |  | vdot VZHK1 4481 | 4481 | vdot_hc1_flow | 4481
| return TRH2 2357 | 2357 | t_hc2_return | 2357 |  | ventilstellung RV_HK1 4473 | 4473 | vent_hc1 | 4473
| vdot VZHK2 2598 | 2598 | vdot_hc2_feedflow | 2598 | HK2 | flow TVH2 4376 | 4376 | t_hc2_flow | 4376
| Ventilstellung RV_HK2 2590 | 2590 | vent_hc2 | 2590 |  | return TRH2 4268 | 4268 | t_hc2_return | 4268
| Mix2 | 13213 | t_mix2 | 13213 |  | vdot VZHK2 4511 | 4511 | vdot_hc2_flow | 4511
WP1 | flow TVHGWP1 2483 | 2483 | t_hp1_hg_flow | 2483 |  | ventilstellung RV_HK2 4503 | 4503 | vent_hc2 | 4503
| return TRHGWP1 2364 | 2364 | t_hp1_hg_return | 2364 | HK | flow | 14108 | t_hctot_flow | 14108
| flow TVSWP1 2518 | 2518 | t_hp1_flow | 2518 |  | return | 14109 | t_hctot_return | 14109
| return TRSWP1 2399 | 2399 | t_hp1_return | 2399 | WP1 | flow TVHGWP1 4364 | 4364 | t_hp1_hg_flow | 4364
| vdot VZHGWP1 2546 | 2546 | vdot_hp1_hg_flow | 2546 |  | return TRHGWP1 4256 | 4256 | t_hp1_hg_return | 4256
| vdot VZWP1 2550 | 2550 | vdot_hp1_flow | 2550 |  | flow TVSWP1 4406 | 4406 | t_hp1_flow | 4406
| pel PEEZWP1 2678 | 2678 | pel_hp1 | 2678 |  | return TRSWP1 4310 | 4310 | t_hp1_return | 4310
| Mix1 | 13212 | t_mix1 | 13212 |  | vdot VZHGWP1 4447 | 4447 | vdot_hp1_hg_flow | 4447
WP2 | flow TVSWP2 2525 | 2525 | t_hp2_flow | 2525 |  | vdot VZSWP1 4451 | 4451 | vdot_hp1_flow | 4451
| return TRSWP2 2406 | 2406 | t_hp2_return | 2406 |  | pel PEZWP1 4615 | 4615 | pel_hp1 | 4615
| vdot VZWP2 2564 | 2564 | vdot_hp2_flow | 2564 | WP2 | flow TVSWP2 4412 | 4412 | t_hp2_flow | 4412
| pel PEEZWP2 2681 | 2681 | pel_hp2 | 2681 |  | return TRSWP2 4316 | 4316 | t_hp2_return | 4316
Solar loading | flow TVL 2490 | 2490 | t_sl_flow | 2490 |  | vdot VZWP2 4467 | 4467 | vdot_hp2_flow | 4467
| return TRL 2371 | 2371 | t_sl_return | 2371 |  | pel PEZWP2 4619 | 4619 | pel_hp2 | 4619
| vdot VZLK 2673 | 2673 | vdot_sl | 2673 | Loading circuit | flow TVL 4388 | 4388 | t_load_flow | 4388
| Pumpe PU_L 2652 | 2652 | s_sl_pump | 2652 |  | return TRL 4286 | 4286 | t_load_return | 4286
Heat Rod | pel PEZ HS | 2684 | pel_hr | 2684 |  | vdot VZL 4587 | 4587 | vdot_load | 4587
| e EZ HS | 2683 |  |  |  | Pump PU_L 4593 | 4593 | s_load_pump | 4593
[5 empty] | Boiler K | flow TVK 4382 | 4382 | t_b_flow | 4382
[6 empty] | return TRK 4280 | 4280 | t_b_return | 4280
[6 empty] | vdot VZK 4428 | 4428 | vdot_b | 4428
[6 empty] | Status boiler | 4417 | s_b | 4417
[6 empty] | Boiler malfunction 7367 | 7367 | mf_b | 7367
[6 empty] | vdot gas | 4414 | vdot_b_gas | 4414
[5 empty] | Solar (prim) | flow TSK 4328 | 4328 | t_sol_flow | 4328
[6 empty] | return1 TSQ 4334 | 4334 | t_sol1_return | 4334
[6 empty] | return1 TSR 4340 | 4340 | t_sol2_return | 4340
[6 empty] | collector TSK 4322 | 4322 | t_sol_collector | 4322
[6 empty] | vdot VZSK 4544 | 4544 | vdot_sol | 4544
[6 empty] | Pump PU_SK 4550 | 4550 | s_sol_pump | 4550
[5 empty] | Collector (sec) | flow | 14106 | t_sl_flow | 14106
[6 empty] | return | 14107 | t_sl_return | 14107
[6 empty] | Pump PU_SPK 4603 | 4603 | s_sl_pump | 4603

## Seeweg Original
Tank | 2080 mm
Connection | Sensor h in mm (floor) | Connection h in mm (floor) | outlet in the tank | connection 10 (4 opening Schichtlader) | Volume in l (downwards) | dz |  |  |  | Connection | Sensor h in mm (floor) | Connection h in mm (floor) | outlet in the tank | connection 10 (4 opening Schichtlader) | Volume in l (downwards) | dz
top |  | 2080 |  |  | 113 | 320 |  | connection input and output differs |  | top |  | 1990 |  |  | 113 | 320
1 | 1760 | 1760 | 2000 |  | 97 | 200 |  | connection 10 output is a Schichtlader |  | 1 | 1760 | 1760 | 2000 |  | 97 | 200
2 |  | 1560 |  | 1536 | 48 | 100 |  |  |  | 2 |  | 1560 |  | 1536 | 48 | 100
3 |  | 1460 |  |  | 48 | 100 |  |  |  | 3 |  | 1460 |  |  | 48 | 100
4 | 1360 | 1360 |  |  | 48 | 100 |  |  |  | 4 | 1360 | 1360 |  |  | 48 | 100
5 |  | 1260 |  | 1239 | 48 | 100 |  |  |  | 5 |  | 1260 |  | 1239 | 48 | 100
6 | 1160 | 1160 |  | 942 | 152 | 315 |  |  |  | 6 | 1160 | 1160 |  | 942 | 152 | 315
7 | 845 | 845 |  |  | 48 | 100 |  |  |  | 7 | 845 | 845 |  |  | 48 | 100
8 |  | 745 |  | 645 | 169 | 350 |  |  |  | 8 |  | 745 |  | 645 | 169 | 350
9 | 395 | 395 |  |  | 0 | 0 |  |  |  | 9 | 395 | 395 |  |  | 0 | 0
10 |  | 395 |  |  | 60 | 125 |  |  |  | 10 |  | 395 |  |  | 60 | 125
11 | 270 | 270 | 120 |  | 0 | 0 |  |  |  | 11 | 270 | 270 | 120 |  | 0 | 0
12 |  | 270 | 120 |  | 74 | 210 |  |  |  | 12 |  | 153 | 3 |  | 74 | 210
bottom |  | 61 |  |  |  | 60 |  |  |  | bottom |  | 117 |  |  |  | 60
floor |  | 0 |  |  |  | 2080 |  |  |  | floor |  | 0 |  |  |  | 2080
Total important points | distance floor | distance tank bottom | 10 layers | 6 layers |  | 6 |  | 10
top | 2080 | 2020 | 9 | 5 | 4 | 2020 | 5 | 2020 | 9
c1 (+240) | 2000 | 1940 | [5 empty] | 1818 | 8
t1 | 1760 | 1700 | 8 |  |  | 1683.3333 | 4 | 1616 | 7
c2 | 1560 | 1500 | 7 | 4 | 3
l1 | 1536 | 1476 | [5 empty] | 1414 | 6
c3 | 1460 | 1400 | 6 |  |  | 1346.6667 | 3
c4, t2 | 1360 | 1300 |  | 3 | 2 |  |  | 1212 | 5
c5 | 1260 | 1200 | 5
l2 | 1239 | 1179 |  |  |  | 1010 | 2 | 1010 | 4
c6, t3 | 1160 | 1100
l3 | 942 | 882 | 4 | 2 | 1 |  |  | 808 | 3
c7, t4 | 845 | 785 | 3
c8 | 745 | 685 |  |  |  | 673.3333 | 1 | 606 | 2
l4 | 645 | 585 | 2 | 1 | 0 | 336.6667 | 0 | 404 | 1
c9, t5 | 395 | 335 | 1 | 0
t6 | 270 | 210
c11, c12 (-150) | 120 | 60 | 0 |  |  |  |  | 202 | 0
bottom | 60 | 0 |  |  |  | 0 |  | 0
Tank with 10 layers
dz = 202 mm | beginn layer | end layer | middle layer | sensor | sensor height | sensor position relation to middle of layer | connection | [6 empty] | Tank with 6 layers
9 | 1818 | 2020 | 1919 | - |  |  | c1 | [6 empty] | dz = 337 | beginn | end | middle | sensor | height sensor | sensor position relation to middle of layer | connection
8 | 1616 | 1818 | 1717 | t1 | 1700 | -8.416% | - | 10 layers offer us 5 validation points located close to the middle of the layer | [5 empty] | 5 | 1683.3333 | 2020 | 1851.6667 | t1 | 1700 | -45% | c1
7 | 1414 | 1616 | 1515 | - |  |  | c2, l1 |  | Sensor location is almost middle of tank |  |  |  |  | 4 | 1346.6667 | 1683.3333 | 1515 | - |  |  | c2, c3, l1
6 | 1212 | 1414 | 1313 | t2 | 1300 | -6.436% | c3, c4 |  | Sensor location is close to middle of tank |  |  |  |  | 3 | 1010 | 1346.6667 | 1178.3333 | t3, t2 | 1100 | -23.24% | c4, c5, c6, l2
5 | 1010 | 1212 | 1111 | t3 | 1100 | -5.446% | c5, c6, l2 |  | Sensor location is far from middle of tank |  |  |  |  | 2 | 673.3333 | 1010 | 841.6667 | t4 | 785 | -16.82% | c7, c8, l3
4 | 808 | 1010 | 909 | - |  |  | l3 | [6 empty] | 1 | 336.6667 | 673.3333 | 505 | - |  |  | l4
3 | 606 | 808 | 707 | t4 | 785 | 38.61% | c7, c8 |  | Schichtenlader |  |  |  |  | 0 | 0 | 336.6667 | 168.3333 | t6, t5 | 210 | 12.36% | c9, c11, c12
2 | 404 | 606 | 505 | - |  |  | l4
1 | 202 | 404 | 303 | t5 (, t6) | 335 | 15.84% | c9
0 | 0 | 202 | 101 | - (t6 is 210) |  |  | c11,c12
Name of the stream | Composition | Temperature | Volume rate | Sensor
m9 | c1 | t_hc1_feedflow | vdot_hc1_feedflow
m8 | - | - | - | t_sp1
m7 |  | c2, l1
m6 |  | c3, c4
m5 |  | c5, c6, l2
m4 |  | l3
m3 |  | c7, c8
m2 |  | l4
m1 |  | c9
m0 |  | c11,c12

## Seeweg V const
Tank | 2080 mm
Connection | Sensor h in mm (floor) | Connection h in mm (floor) | outlet in the tank | connection 10 (4 opening Schichtlader) | Volume in l (downwards) | dz in mm
top |  | 1990 |  |  | 113 | 230 |  | connection input and output differs
1 | 1760 | 1760 | 200 |  | 97 | 200 |  | connection 10 output is a Schichtlader
2 |  | 1560 |  | 1536 | 48 | 100
3 |  | 1460 |  |  | 48 | 100
4 | 1360 | 1360 |  |  | 48 | 100
5 |  | 1260 |  | 1239 | 48 | 100
6 | 1160 | 1160 |  | 942 | 152 | 315
7 | 845 | 845 |  |  | 48 | 100
8 |  | 745 |  | 645 | 169 | 350
9 | 395 | 395 |  |  | 0 | 0
10 |  | 395 |  |  | 60 | 125
11 | 270 | 153 | -150 |  | 0 | 0
12 |  | 153 | -150 |  | 74 | 153
bottom |  | 117 |  |  |  | 117
floor |  | 0
|  |  |  | Sum | 905 | 1990
Total important points | distance floor | distance tank bottom | 10 layers | 6 layers |  | 6 |  | 10
top | 1990 | 1873 | 9 | 5 |  | 1873 | 5 | 1873 | 9
p1 (+200) | 1960 | 1843 | [5 empty] | 1685.7 | 8
t1 | 1760 | 1643 | 8 |  |  | 1560.8333 | 4 | 1498.4 | 7
p2 | 1560 | 1443 | 7 | 4
l1 | 1536 | 1419 | [5 empty] | 1311.1 | 6
p3 | 1460 | 1343 |  |  |  | 1248.6667 | 3
p4, t2 | 1360 | 1243 | 6 | 3 |  |  |  | 1123.8 | 5
p5 | 1260 | 1143
l2 | 1239 | 1122 | 5 |  |  | 936.5 | 2 | 936.5 | 4
p6, t3 | 1160 | 1043
l3 | 942 | 825 | 4 | 2 |  |  |  | 749.2 | 3
p7, t4 | 845 | 728 | 3
p8 | 745 | 628 |  |  |  | 624.3333 | 1 | 561.9 | 2
l4 | 645 | 528 | 2 | 1 |  | 312.1667 | 0 | 374.6 | 1
p9, t5 | 395 | 278 | 1 | 0
t6 | 270 | 153 | 0
p11, p12 (-150) | 153 | 36 | [5 empty] | 187.3 | 0
bottom | 117 | 0 |  |  |  | 0 |  | 0
Tank with 10 layers | [9 empty] | Tank with 6 layers
187.3 | beginn layer | end layer | middle layer | sensor | sensor height | sensor position relation to middle of layer | connection |  |  | 312.1667 | beginn layer | end layer | middle layer | sensor | sensor height | sensor position relation to middle of layer | connection
9 | 1685.7 | 1873 | 1779.35 | - |  |  | p1 |  |  | 5 | 1560.8333 | 1873 | 1716.9167 | t1 | 1643 | -78.93% | p1
8 | 1498.4 | 1685.7 | 1592.05 | t1 | 1643 | 54.4% | - |  |  | 4 | 1248.6667 | 1560.8333 | 1404.75 | - |  |  | p2, p3, l1
7 | 1311.1 | 1498.4 | 1404.75 | - |  |  | p2, p3, l1 |  |  | 3 | 936.5 | 1248.6667 | 1092.5833 | t3 (t2) | 1043 | -52.95% | p4, p5, p6, l2
6 | 1123.8 | 1311.1 | 1217.45 | t2 | 1243 | 27.28% | p4, p5 |  |  | 2 | 624.3333 | 936.5 | 780.4167 | t4 | 728 | -55.97% | p7, p8, l3
5 | 936.5 | 1123.8 | 1030.15 | t3 | 1043 | 13.72% | p6, l2 |  |  | 1 | 312.1667 | 624.3333 | 468.25 | - |  |  | l4
4 | 749.2 | 936.5 | 842.85 |  |  |  | l3 |  |  | 0 | 0 | 312.1667 | 156.0833 | t6 (t5) | 153 | -3.292% | p9, p11, p12
3 | 561.9 | 749.2 | 655.55 | t4 | 728 | 77.36% | p7, p8
2 | 374.6 | 561.9 | 468.25 | - |  |  | l4
1 | 187.3 | 374.6 | 280.95 | t5 | 278 | -3.15% | p9
0 | 0 | 187.3 | 93.65 | t6 | 153 | 63.37% | p11,p12
Name of the stream | Composition (position) | composition (connection) |  |  |  | 93.65 | 1217.45 | 1311.1
m9 | p1 | c1 |  |  |  |  | -25.55
m8 | - | [5 empty] | -27.28%
m7 | p2, l1 | c2, l1
m6 | p3, p4 | e1, c3
m5 | p5, p6, l2
m4 | l3
m3 | p7, p8
m2 | l4
m1 | p9
m0 | p11,p12
Connection | Position | Temperature | Volume rate | Power
c1 | p1 | t_hc1_feedflow | - vdot_hc1_feedflow
c2 | p2 | t_hp1_hg_flow | vdot_hp1_hg_flow
c3 | p4 | t_hp1_hg_return | - vdot_hp1_hg_flow
c4 | p6 | vdot_hc1_feedflow*valve_hc1_return | vdot_hc1_feedflow1
c5 | p7 | t_hc2_feedflow | - vdot_hc2_feedflow
c6 | p8 | t_hp2_flow | vdot_hp2_flow
c7 | p9 | t_mix2 | vdot_hc2_feedflow - vdot_hp2_flow
c8 | p10 | t_mix1 | vdot_sl + vdot_hp1_flow
c9 | p11 | t_hc1_return | valve_hc1_return * inverse_valve
c10 | p12 | t_hp1_return | - (vdot_sl + vdot_hp1_flow)
e1 | p3 | / | / | pel_hr
Note on D6: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: Assumption: since actual internal outlet of c1 has dz = 240 and this is higher than our assumpted height of the tank, we will assume a dz of 200